## Executive Summary
Al Fou'ah 3380 Students School — Executive Summary
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Project | Al Fou'ah 3380 Students School
Client | Department of Education and Knowledge
Consultant | Altorath International Engineering Consultants
Contractor
Location | Dubai, UAE
Building Type | School
Scope of Work | ELV / Low Current Package
Number of Floors | 3
Area | 18500 sqm
Required Systems | CCTV, Access Control, Structured Cabling, Wi-Fi, Parking Management
Export Type | full
Generated | 8/17/2026, 5:38:25 PM
Total Consolidated BOQ Items | 10
Total Systems | 4
Total Drawings | 1
Average AI Confidence | 83%
Items Requiring Review | 5
Items Requiring Engineer Approval | 1
Duplicate drawing uploads excluded | 0

## Consolidated BOQ
Al Fou'ah 3380 Students School — Consolidated BOQ
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Item Code | System | Item Name | Specification | Manufacturer | Model | Building/Villa | Floor(s) | Zone(s) | Room(s) | Location | Unit | Total Quantity | Confidence % | Status | Physical Sources | Reference Sources (not counted) | Quantity Discrepancy
CCTV-003 | CCTV | 18U CCTV Equipment Rack, lockable, with PDU and cable management | 600x600mm floor standing 18U |  |  | B01 School Main Building | SF | SF/West Wing | SF/IDF Room S.318 | IDF Room S.318 | nos | 2 | 92 | confirmed | 1 | 0
SCS-001 | Structured Cabling | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | 500MHz LSZH, security distribution |  |  | B01 School Main Building | SF | SF/West Wing | SF/High level trunk | High level trunk | m | 150 | 70 | review_required | 1 | 0
CCTV-002 | CCTV | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | 2MP dome, vandal resistant, lift car mount |  |  | B01 School Main Building | SF | SF/West Wing | SF/Lift Car | Lift Car | nos | 1 | 90 | confirmed | 1 | 0
CCTV-001 | CCTV | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | 2MP IP indoor dome, PoE 802.3af, IR 30m, IP66 |  |  | B01 School Main Building | SF | SF/West Wing | SF/S.315 Classroom | S.315 Classroom | nos | 7 | 95 | confirmed | 1 | 0
ACS-001 | Access Control | Door Access Control Reader, proximity card type, surface mounted | IP reader, PoE, OSDP |  |  | B01 School Main Building | SF | SF/West Wing | SF/Classroom doors | Classroom doors | nos | 34 | 85 | review_required | 1 | 0
ACS-002 | Access Control | Electromagnetic Door Lock (Maglock) with door position sensor | 280kg holding force, 12/24VDC failsafe |  |  | B01 School Main Building | SF | SF/West Wing | SF/Door head | Door head | nos | 34 | 75 | review_required | 1 | 0
ACS-003 | Access Control | Exit Push Button | Stainless steel, press to exit |  |  | B01 School Main Building | SF | SF/West Wing | SF/Inside door | Inside door | nos | 34 | 100 | confirmed | 1 | 0
CONT-001 | Containment | GI Cable Trunk 75x75mm, hot dip galvanised | 75x75mm GI trunk with covers |  |  | B01 School Main Building | SF | SF/West Wing | SF/Corridor high level | Corridor high level | m | 80 | 65 | engineer_review | 1 | 0
SCS-003 | Structured Cabling | Patch Cord CAT6A 2m LSZH, factory terminated | Derived accessory |  |  | B01 School Main Building | SF | SF/West Wing | SF/Various | Various | nos | 82 | 80 | review_required | 1 | 0
SCS-002 | Structured Cabling | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | Derived accessory |  |  | B01 School Main Building | SF | SF/West Wing | SF/Various | Various | nos | 41 | 80 | review_required | 1 | 0

## Master BOQ (Full Detail)
Al Fou'ah 3380 Students School — Master BOQ (Full Detail)
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Item Code | System | Subsystem | Building/Villa | Item Name | Technical Specification | Manufacturer | Model | Floor(s) | Zone(s) | Room(s) | Unit | Total Quantity | Calculation / Quantity Basis | Optimization Status | Optimization Note | Confidence % | Compliance Status | Compliance Notes | Status | Drawing Source(s) | Quantity Discrepancy
CCTV-003 | CCTV |  | B01 School Main Building | 18U CCTV Equipment Rack, lockable, with PDU and cable management | 600x600mm floor standing 18U |  |  | SF | SF/West Wing | SF/IDF Room S.318 | nos | 2 | Counted 2 symbols on SHEET 8 | Drawing Requirement |  | 92 | ok |  | confirmed | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
SCS-001 | Structured Cabling |  | B01 School Main Building | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | 500MHz LSZH, security distribution |  |  | SF | SF/West Wing | SF/High level trunk | m | 150 | Counted 150 symbols on SHEET 8 | Drawing Requirement |  | 70 | ok |  | review_required | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
CCTV-002 | CCTV |  | B01 School Main Building | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | 2MP dome, vandal resistant, lift car mount |  |  | SF | SF/West Wing | SF/Lift Car | nos | 1 | Counted 1 symbols on SHEET 8 | Drawing Requirement |  | 90 | ok |  | confirmed | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
CCTV-001 | CCTV |  | B01 School Main Building | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | 2MP IP indoor dome, PoE 802.3af, IR 30m, IP66 |  |  | SF | SF/West Wing | SF/S.315 Classroom | nos | 7 | Counted 7 symbols on SHEET 8 | Drawing Requirement |  | 95 | ok |  | confirmed | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
ACS-001 | Access Control |  | B01 School Main Building | Door Access Control Reader, proximity card type, surface mounted | IP reader, PoE, OSDP |  |  | SF | SF/West Wing | SF/Classroom doors | nos | 34 | Counted 34 symbols on SHEET 8 | Drawing Requirement |  | 85 | ok |  | review_required | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
ACS-002 | Access Control |  | B01 School Main Building | Electromagnetic Door Lock (Maglock) with door position sensor | 280kg holding force, 12/24VDC failsafe |  |  | SF | SF/West Wing | SF/Door head | nos | 34 | Counted 34 symbols on SHEET 8 | Drawing Requirement |  | 75 | ok |  | review_required | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
ACS-003 | Access Control |  | B01 School Main Building | Exit Push Button | Stainless steel, press to exit |  |  | SF | SF/West Wing | SF/Inside door | nos | 34 | Counted 34 symbols on SHEET 8 | Drawing Requirement |  | 100 | ok |  | confirmed | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
CONT-001 | Containment |  | B01 School Main Building | GI Cable Trunk 75x75mm, hot dip galvanised | 75x75mm GI trunk with covers |  |  | SF | SF/West Wing | SF/Corridor high level | m | 80 | Counted 80 symbols on SHEET 8 | Drawing Requirement |  | 65 | ok |  | engineer_review | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
SCS-003 | Structured Cabling |  | B01 School Main Building | Patch Cord CAT6A 2m LSZH, factory terminated | Derived accessory |  |  | SF | SF/West Wing | SF/Various | nos | 82 | Counted 82 symbols on SHEET 8 | Engineered |  | 80 | ok |  | review_required | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf
SCS-002 | Structured Cabling |  | B01 School Main Building | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | Derived accessory |  |  | SF | SF/West Wing | SF/Various | nos | 41 | Counted 41 symbols on SHEET 8 | Engineered |  | 80 | ok |  | review_required | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf

## Simple BOQ
Al Fou'ah 3380 Students School — Simple BOQ
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Line | System | Item Description | Building / Floor(s) | Qty | Unit | Status | Remarks
1 | Access Control | Door Access Control Reader, proximity card type, surface mounted | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
2 | Access Control | Electromagnetic Door Lock (Maglock) with door position sensor | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
3 | Access Control | Exit Push Button | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
4 | CCTV | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | B01 School Main Building – SF | 1 | nos | Confirmed | Counted 1 symbols on SHEET 8
5 | CCTV | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | B01 School Main Building – SF | 7 | nos | Confirmed | Counted 7 symbols on SHEET 8
6 | CCTV | 18U CCTV Equipment Rack, lockable, with PDU and cable management | B01 School Main Building – SF | 2 | nos | Confirmed | Counted 2 symbols on SHEET 8
7 | Containment | GI Cable Trunk 75x75mm, hot dip galvanised | B01 School Main Building – SF | 80 | m | Confirmed | Counted 80 symbols on SHEET 8
8 | Structured Cabling | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | B01 School Main Building – SF | 41 | nos | Engineered | Counted 41 symbols on SHEET 8
9 | Structured Cabling | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | B01 School Main Building – SF | 150 | m | Confirmed | Counted 150 symbols on SHEET 8
10 | Structured Cabling | Patch Cord CAT6A 2m LSZH, factory terminated | B01 School Main Building – SF | 82 | nos | Engineered | Counted 82 symbols on SHEET 8

## System BOQ
Al Fou'ah 3380 Students School — System BOQ
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
System | BOQ Items | Confirmed | Review Required | Engineer Review | Avg. Confidence %
CCTV | 3 | 3 | 0 | 0 | 92
Structured Cabling | 3 | 0 | 3 | 0 | 77
Access Control | 3 | 1 | 2 | 0 | 87
Containment | 1 | 0 | 0 | 1 | 65

## Floor Breakdown
Al Fou'ah 3380 Students School — Floor Breakdown
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Item Code | Item Name | Floor | Source Label(s) | Quantity | Unit
CCTV-003 | 18U CCTV Equipment Rack, lockable, with PDU and cable management | SF | Second Floor | 2 | nos
SCS-001 | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | SF | Second Floor | 150 | m
CCTV-002 | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | SF | Second Floor | 1 | nos
CCTV-001 | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | SF | Second Floor | 7 | nos
ACS-001 | Door Access Control Reader, proximity card type, surface mounted | SF | Second Floor | 34 | nos
ACS-002 | Electromagnetic Door Lock (Maglock) with door position sensor | SF | Second Floor | 34 | nos
ACS-003 | Exit Push Button | SF | Second Floor | 34 | nos
CONT-001 | GI Cable Trunk 75x75mm, hot dip galvanised | SF | Second Floor | 80 | m
SCS-003 | Patch Cord CAT6A 2m LSZH, factory terminated | SF | Second Floor | 82 | nos
SCS-002 | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | SF | Second Floor | 41 | nos

## Zone Breakdown
Al Fou'ah 3380 Students School — Zone Breakdown
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Item Code | Item Name | Floor | Zone | Quantity | Unit
CCTV-003 | 18U CCTV Equipment Rack, lockable, with PDU and cable management | SF | West Wing | 2 | nos
SCS-001 | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | SF | West Wing | 150 | m
CCTV-002 | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | SF | West Wing | 1 | nos
CCTV-001 | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | SF | West Wing | 7 | nos
ACS-001 | Door Access Control Reader, proximity card type, surface mounted | SF | West Wing | 34 | nos
ACS-002 | Electromagnetic Door Lock (Maglock) with door position sensor | SF | West Wing | 34 | nos
ACS-003 | Exit Push Button | SF | West Wing | 34 | nos
CONT-001 | GI Cable Trunk 75x75mm, hot dip galvanised | SF | West Wing | 80 | m
SCS-003 | Patch Cord CAT6A 2m LSZH, factory terminated | SF | West Wing | 82 | nos
SCS-002 | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | SF | West Wing | 41 | nos

## Procurement BOQ
Al Fou'ah 3380 Students School — Procurement BOQ
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Item No. | System | Item Name | Detailed Specification | Manufacturer | Model | Unit | Total Quantity | Required Accessories | Spare % | Final Procurement Quantity | Status
CCTV-003 | CCTV | 18U CCTV Equipment Rack, lockable, with PDU and cable management | 600x600mm floor standing 18U |  |  | nos | 2 |  | 5% | 3 | confirmed
SCS-001 | Structured Cabling | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | 500MHz LSZH, security distribution |  |  | m | 150 |  | 10% | 165 | review_required
CCTV-002 | CCTV | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | 2MP dome, vandal resistant, lift car mount |  |  | nos | 1 |  | 5% | 2 | confirmed
CCTV-001 | CCTV | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | 2MP IP indoor dome, PoE 802.3af, IR 30m, IP66 |  |  | nos | 7 |  | 5% | 8 | confirmed
ACS-001 | Access Control | Door Access Control Reader, proximity card type, surface mounted | IP reader, PoE, OSDP |  |  | nos | 34 |  | 5% | 36 | review_required
ACS-002 | Access Control | Electromagnetic Door Lock (Maglock) with door position sensor | 280kg holding force, 12/24VDC failsafe |  |  | nos | 34 |  | 5% | 36 | review_required
ACS-003 | Access Control | Exit Push Button | Stainless steel, press to exit |  |  | nos | 34 |  | 5% | 36 | confirmed
CONT-001 | Containment | GI Cable Trunk 75x75mm, hot dip galvanised | 75x75mm GI trunk with covers |  |  | m | 80 |  | 10% | 88 | engineer_review
SCS-003 | Structured Cabling | Patch Cord CAT6A 2m LSZH, factory terminated | Derived accessory |  |  | nos | 82 |  | 10% | 91 | review_required
SCS-002 | Structured Cabling | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | Derived accessory |  |  | nos | 41 |  | 10% | 46 | review_required

## Engineering BOQ
Al Fou'ah 3380 Students School — Engineering BOQ
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
System | Item | Quantity | Unit | Design Basis | Testing / Commissioning | Confidence % | Source
CCTV | 18U CCTV Equipment Rack, lockable, with PDU and cable management | 2 | nos | 600x600mm floor standing 18U | IEC 62676 functional test | 92 | ai_drawing_analysis
Structured Cabling | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | 150 | m | 500MHz LSZH, security distribution | IEC 62676 functional test | 70 | ai_drawing_analysis
CCTV | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | 1 | nos | 2MP dome, vandal resistant, lift car mount | IEC 62676 functional test | 90 | ai_drawing_analysis
CCTV | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | 7 | nos | 2MP IP indoor dome, PoE 802.3af, IR 30m, IP66 | IEC 62676 functional test | 95 | ai_drawing_analysis
Access Control | Door Access Control Reader, proximity card type, surface mounted | 34 | nos | IP reader, PoE, OSDP | IEC 62676 functional test | 85 | ai_drawing_analysis
Access Control | Electromagnetic Door Lock (Maglock) with door position sensor | 34 | nos | 280kg holding force, 12/24VDC failsafe | IEC 62676 functional test | 75 | ai_drawing_analysis
Access Control | Exit Push Button | 34 | nos | Stainless steel, press to exit | IEC 62676 functional test | 100 | ai_drawing_analysis
Containment | GI Cable Trunk 75x75mm, hot dip galvanised | 80 | m | 75x75mm GI trunk with covers | IEC 62676 functional test | 65 | ai_drawing_analysis
Structured Cabling | Patch Cord CAT6A 2m LSZH, factory terminated | 82 | nos | Derived accessory | IEC 62676 functional test | 80 | engineering_rule
Structured Cabling | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | 41 | nos | Derived accessory | IEC 62676 functional test | 80 | engineering_rule

## Review Required
Al Fou'ah 3380 Students School — Review Required
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Item Code | System | Item Name | Quantity | Unit | Confidence % | Source Count
SCS-001 | Structured Cabling | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | 150 | m | 70 | 1
ACS-001 | Access Control | Door Access Control Reader, proximity card type, surface mounted | 34 | nos | 85 | 1
ACS-002 | Access Control | Electromagnetic Door Lock (Maglock) with door position sensor | 34 | nos | 75 | 1
SCS-003 | Structured Cabling | Patch Cord CAT6A 2m LSZH, factory terminated | 82 | nos | 80 | 1
SCS-002 | Structured Cabling | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | 41 | nos | 80 | 1

## Engineer Review
Al Fou'ah 3380 Students School — Engineer Review
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Item Code | System | Item Name | Quantity | Unit | Confidence % | Source Count
CONT-001 | Containment | GI Cable Trunk 75x75mm, hot dip galvanised | 80 | m | 65 | 1

## Drawing Evidence
Al Fou'ah 3380 Students School — Drawing Evidence
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Item Code | Item Name | Drawing | Page | Floor (raw) | Floor (normalized) | Zone | Quantity | Source Type | Counted Toward Total? | Confidence % | Location | Basis Notes
CCTV-003 | 18U CCTV Equipment Rack, lockable, with PDU and cable management | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf | 1 | Second Floor | SF | West Wing | 2 | Physical Count | Yes | 92 | IDF Room S.318 | Counted 2 symbols on SHEET 8
SCS-001 | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf |  | Second Floor | SF | West Wing | 150 | Physical Count | Yes | 70 | High level trunk | Counted 150 symbols on SHEET 8
CCTV-002 | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf | 1 | Second Floor | SF | West Wing | 1 | Physical Count | Yes | 90 | Lift Car | Counted 1 symbols on SHEET 8
CCTV-001 | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf | 1 | Second Floor | SF | West Wing | 7 | Physical Count | Yes | 95 | S.315 Classroom | Counted 7 symbols on SHEET 8
ACS-001 | Door Access Control Reader, proximity card type, surface mounted | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf | 1 | Second Floor | SF | West Wing | 34 | Physical Count | Yes | 85 | Classroom doors | Counted 34 symbols on SHEET 8
ACS-002 | Electromagnetic Door Lock (Maglock) with door position sensor | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf | 1 | Second Floor | SF | West Wing | 34 | Physical Count | Yes | 75 | Door head | Counted 34 symbols on SHEET 8
ACS-003 | Exit Push Button | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf | 1 | Second Floor | SF | West Wing | 34 | Physical Count | Yes | 100 | Inside door | Counted 34 symbols on SHEET 8
CONT-001 | GI Cable Trunk 75x75mm, hot dip galvanised | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf |  | Second Floor | SF | West Wing | 80 | Physical Count | Yes | 65 | Corridor high level | Counted 80 symbols on SHEET 8
SCS-003 | Patch Cord CAT6A 2m LSZH, factory terminated | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf |  | Second Floor | SF | West Wing | 82 | Calculated Quantity | Yes | 80 | Various | Counted 82 symbols on SHEET 8
SCS-002 | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf |  | Second Floor | SF | West Wing | 41 | Calculated Quantity | Yes | 80 | Various | Counted 41 symbols on SHEET 8

## Revision History
Al Fou'ah 3380 Students School — Revision History
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Drawing | Revision | Status | Change Reason | Approval Status | Created
AAFOS-BW-AIC-ZZ-B1-02-PL-SC-00308-SECOND FLOOR SECURITY LAYOUT SHEET 8.pdf | 2 | completed |  |  | 2026-08-17T08:11:00.000Z

## Cost Optimizations
Al Fou'ah 3380 Students School — Cost Optimizations
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Title | Related Item | Original Approach | Optimized Approach | Estimated Savings | Status

## Assumptions
Al Fou'ah 3380 Students School — Assumptions
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Assumption | Related Item

## Engineer Review Items
Al Fou'ah 3380 Students School — Engineer Review Items
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Reason | Related Item | Status

## Project Specification
Al Fou'ah 3380 Students School — Project Specification
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
System | Requirement | Description | Parameter | Required Value | Specified Brands | Approved Equal | Standards | Certifications | Origin Restriction | Qty in Spec | Unit | Clause | Page | Confidence %
CCTV | Fixed Dome Camera — internal areas | Internal dome cameras to classrooms, corridors and lobbies, recording to the central VMS. | Resolution | 4 MP minimum | Axis, Hanwha, Bosch | Yes | IEC 62676-1, EN 50132 | SIRA approval, CE | EU, USA, Japan or Korea |  | no | 27 20 10.3 | 148 | 92
CCTV | Fixed Dome Camera — internal areas | Internal dome cameras to classrooms, corridors and lobbies, recording to the central VMS. | Lens | 2.8–12 mm motorised varifocal | Axis, Hanwha, Bosch | Yes | IEC 62676-1, EN 50132 | SIRA approval, CE | EU, USA, Japan or Korea |  | no | 27 20 10.3 | 148 | 92
CCTV | Fixed Dome Camera — internal areas | Internal dome cameras to classrooms, corridors and lobbies, recording to the central VMS. | IR range | 30 m minimum | Axis, Hanwha, Bosch | Yes | IEC 62676-1, EN 50132 | SIRA approval, CE | EU, USA, Japan or Korea |  | no | 27 20 10.3 | 148 | 92
CCTV | Fixed Dome Camera — internal areas | Internal dome cameras to classrooms, corridors and lobbies, recording to the central VMS. | Ingress protection | IP66 | Axis, Hanwha, Bosch | Yes | IEC 62676-1, EN 50132 | SIRA approval, CE | EU, USA, Japan or Korea |  | no | 27 20 10.3 | 148 | 92
CCTV | Fixed Dome Camera — internal areas | Internal dome cameras to classrooms, corridors and lobbies, recording to the central VMS. | Impact rating | IK10 vandal resistant | Axis, Hanwha, Bosch | Yes | IEC 62676-1, EN 50132 | SIRA approval, CE | EU, USA, Japan or Korea |  | no | 27 20 10.3 | 148 | 92
CCTV | Fixed Dome Camera — internal areas | Internal dome cameras to classrooms, corridors and lobbies, recording to the central VMS. | Power | PoE IEEE 802.3af | Axis, Hanwha, Bosch | Yes | IEC 62676-1, EN 50132 | SIRA approval, CE | EU, USA, Japan or Korea |  | no | 27 20 10.3 | 148 | 92
CCTV | Fixed Dome Camera — internal areas | Internal dome cameras to classrooms, corridors and lobbies, recording to the central VMS. | Video analytics | Line crossing and intrusion detection | Axis, Hanwha, Bosch | Yes | IEC 62676-1, EN 50132 | SIRA approval, CE | EU, USA, Japan or Korea |  | no | 27 20 10.3 | 148 | 92
CCTV | Network Video Recorder / VMS Server | Central recording with 31 days retention at full frame rate. | Retention | 31 days minimum | Milestone, Genetec | No | ONVIF Profile S | SIRA approval |  | 1 | no | 27 20 10.7 | 151 | 88
CCTV | Network Video Recorder / VMS Server | Central recording with 31 days retention at full frame rate. | Recording | Full frame rate, all channels | Milestone, Genetec | No | ONVIF Profile S | SIRA approval |  | 1 | no | 27 20 10.7 | 151 | 88
CCTV | Network Video Recorder / VMS Server | Central recording with 31 days retention at full frame rate. | RAID | RAID-5 minimum | Milestone, Genetec | No | ONVIF Profile S | SIRA approval |  | 1 | no | 27 20 10.7 | 151 | 88
CCTV | Network Video Recorder / VMS Server | Central recording with 31 days retention at full frame rate. | Redundancy | Dual power supply | Milestone, Genetec | No | ONVIF Profile S | SIRA approval |  | 1 | no | 27 20 10.7 | 151 | 88
Access Control | Card Reader — classroom and office doors | Proximity reader at every controlled door, integrated with the central ACS. | Technology | MIFARE DESFire EV3 | HID, Suprema | Yes | ISO 14443 | SIRA approval |  | 47 | no | 28 13 00.4 | 163 | 90
Access Control | Card Reader — classroom and office doors | Proximity reader at every controlled door, integrated with the central ACS. | Protocol | OSDP v2 secure channel | HID, Suprema | Yes | ISO 14443 | SIRA approval |  | 47 | no | 28 13 00.4 | 163 | 90
Access Control | Card Reader — classroom and office doors | Proximity reader at every controlled door, integrated with the central ACS. | Power | PoE | HID, Suprema | Yes | ISO 14443 | SIRA approval |  | 47 | no | 28 13 00.4 | 163 | 90
Access Control | Card Reader — classroom and office doors | Proximity reader at every controlled door, integrated with the central ACS. | Mounting | Flush, single gang | HID, Suprema | Yes | ISO 14443 | SIRA approval |  | 47 | no | 28 13 00.4 | 163 | 90
Access Control | Card Reader — classroom and office doors | Proximity reader at every controlled door, integrated with the central ACS. | Ingress protection | IP54 | HID, Suprema | Yes | ISO 14443 | SIRA approval |  | 47 | no | 28 13 00.4 | 163 | 90
Fire Alarm | Addressable Smoke Detector | Optical addressable detectors throughout, on an EN 54 certified loop. | Type | Optical addressable | Notifier, Siemens | Yes | EN 54-7, NFPA 72 | DCD approval |  |  | no | 28 31 00.2 | 201 | 86
Fire Alarm | Addressable Smoke Detector | Optical addressable detectors throughout, on an EN 54 certified loop. | Certification | EN 54-7 | Notifier, Siemens | Yes | EN 54-7, NFPA 72 | DCD approval |  |  | no | 28 31 00.2 | 201 | 86
Fire Alarm | Addressable Smoke Detector | Optical addressable detectors throughout, on an EN 54 certified loop. | Loop | Addressable, class A | Notifier, Siemens | Yes | EN 54-7, NFPA 72 | DCD approval |  |  | no | 28 31 00.2 | 201 | 86

## Take-off BOQ
Al Fou'ah 3380 Students School — Take-off BOQ
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Only what was physically measured off the drawings. Engineered accessories are excluded — see the Designed BOQ sheet.
Line | System | Item Description | Building / Floor(s) | Qty | Unit | Status | Remarks
1 | Access Control | Door Access Control Reader, proximity card type, surface mounted | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
2 | Access Control | Electromagnetic Door Lock (Maglock) with door position sensor | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
3 | Access Control | Exit Push Button | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
4 | CCTV | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | B01 School Main Building – SF | 1 | nos | Confirmed | Counted 1 symbols on SHEET 8
5 | CCTV | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | B01 School Main Building – SF | 7 | nos | Confirmed | Counted 7 symbols on SHEET 8
6 | CCTV | 18U CCTV Equipment Rack, lockable, with PDU and cable management | B01 School Main Building – SF | 2 | nos | Confirmed | Counted 2 symbols on SHEET 8
7 | Containment | GI Cable Trunk 75x75mm, hot dip galvanised | B01 School Main Building – SF | 80 | m | Confirmed | Counted 80 symbols on SHEET 8
8 | Structured Cabling | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | B01 School Main Building – SF | 150 | m | Confirmed | Counted 150 symbols on SHEET 8

## Designed BOQ
Al Fou'ah 3380 Students School — Designed BOQ
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
The complete system: measured items plus the accessories needed to make them work, which no drawing draws. Engineering judgement, not measurement — check every line before pricing.
Line | System | Item Description | Building / Floor(s) | Qty | Unit | Status | Remarks
1 | Access Control | Door Access Control Reader, proximity card type, surface mounted | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
2 | Access Control | Electromagnetic Door Lock (Maglock) with door position sensor | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
3 | Access Control | Exit Push Button | B01 School Main Building – SF | 34 | nos | Confirmed | Counted 34 symbols on SHEET 8
4 | CCTV | CCTV Dome Type Lift Camera (IP) Day & Night, PoE | B01 School Main Building – SF | 1 | nos | Confirmed | Counted 1 symbols on SHEET 8
5 | CCTV | Dome IP CCTV Camera (Day & Night), PoE, Wide Dynamic Range, FHD Resolution, IR Varifocal Lens | B01 School Main Building – SF | 7 | nos | Confirmed | Counted 7 symbols on SHEET 8
6 | CCTV | 18U CCTV Equipment Rack, lockable, with PDU and cable management | B01 School Main Building – SF | 2 | nos | Confirmed | Counted 2 symbols on SHEET 8
7 | Containment | GI Cable Trunk 75x75mm, hot dip galvanised | B01 School Main Building – SF | 80 | m | Confirmed | Counted 80 symbols on SHEET 8
8 | Structured Cabling | RJ45 CAT6A Keystone Jack, LSZH, to each camera and reader | B01 School Main Building – SF | 41 | nos | Engineered | Counted 41 symbols on SHEET 8
9 | Structured Cabling | CAT6A S/UTP Cable, 4-pair 23AWG, LSZH sheath | B01 School Main Building – SF | 150 | m | Confirmed | Counted 150 symbols on SHEET 8
10 | Structured Cabling | Patch Cord CAT6A 2m LSZH, factory terminated | B01 School Main Building – SF | 82 | nos | Engineered | Counted 82 symbols on SHEET 8

## Supplier Comparison
Al Fou'ah 3380 Students School — Supplier Comparison
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Supplier | Currency | Line | Quoted Item | Offered Brand | Offered Model | Origin | Qty | Unit | Unit Rate | Line Value | Compliance | Judged Against | Deviating Parameters | Tender Clause | Tender Page | Assessment | Clarification Needed
Al Fajer Trading LLC | AED | 1 | IP Dome Camera 2MP, fixed 2.8mm lens, IR 20m, IP66 | Dahua | IPC-HDBW2231 | China | 7 | no | 410 | 2870 | Non-compliant | Fixed Dome Camera — internal areas | Resolution: required 4 MP minimum, offered 2 MP ¦ Lens: required 2.8–12 mm motorised varifocal, offered 2.8 mm fixed ¦ IR range: required 30 m minimum, offered 20 m ¦ Impact rating: required IK10 vandal resistant, offered not stated ¦ Origin: required EU, USA, Japan or Korea, offered China | 27 20 10.3 | 148 | The offered camera is 2 MP with a fixed 2.8 mm lens and 20 m IR against a specified minimum of 4 MP, motorised varifocal and 30 m. The brand is not among those specified and the country of origin falls outside the permitted list, so this cannot be accepted as an approved equal on the current information. | Yes
Al Fajer Trading LLC | AED | 2 | NVR 32 channel, 8 bay, RAID 5, 30 days storage | Dahua | NVR5432-EI | China | 1 | no | 9800 | 9800 | Deviation | Network Video Recorder / VMS Server | Retention: required 31 days minimum, offered 30 days ¦ Redundancy: required Dual power supply, offered not stated ¦ Brand: required Milestone or Genetec (no approved equal), offered Dahua | 27 20 10.7 | 151 | Storage falls one day short of the specified 31 days, which is a minor deviation. More significantly the specification names Milestone or Genetec with no approved equal permitted, and a Dahua NVR is offered instead. | Yes
Al Fajer Trading LLC | AED | 3 | Proximity card reader, MIFARE DESFire EV3, OSDP, PoE, IP54 | HID | Signo 20 | USA | 34 | no | 680 | 23120 | Compliant | Card Reader — classroom and office doors |  | 28 13 00.4 | 163 | Fully compliant, and IP65 exceeds the specified IP54.
Al Fajer Trading LLC | AED | 4 | Installation, testing and commissioning — lump sum |  |  |  | 1 | LS | 45000 | 45000 | Not checked | not matched to a requirement
Gulf Security Systems | AED | 1 | 4MP IP Dome, motorised varifocal 2.8-12mm, IR 40m, IP67 IK10 | Hanwha | XND-8081RV | Korea | 7 | no | 960 | 6720 | Compliant | Fixed Dome Camera — internal areas |  | 27 20 10.3 | 148 | Compliant on every specified parameter, with IR range and ingress protection exceeding the minimum.
Gulf Security Systems | AED | 2 | Milestone XProtect Expert, 32 channel licences, RAID-5 server, dual PSU | Milestone | XProtect Expert | Denmark | 1 | no | 18400 | 18400 | Deviation | Network Video Recorder / VMS Server | Redundancy: required Dual power supply, offered single PSU listed | 27 20 10.7 | 151 | Platform and retention are compliant. The server is listed with a single power supply against a specified dual-PSU requirement. | Yes

## Estimation
Al Fou'ah 3380 Students School — Estimation
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Currency | AED
Margin % | 14
Cost to us | 367349
Margin | 51428.86
Sell price | 418777.86
Client budget | 420000
System | Priced Items | Material / Supply | Installation or Subcontract | Cost Subtotal
Access Control | 2 | 41000 | 38500 | 79500
CCTV | 3 | 16000 | 15840 | 31840
Containment | 1 | 7120 | 4500 | 11620
Structured Cabling | 3 | 4389 | 0 | 4389
Project staff / preliminaries |  |  | 240000 | 240000
Total cost |  | 68509 | 298840 | 367349
Margin is applied once to the total cost, not per system — the same way the Estimation page calculates it.
Project staff — breakdown | Headcount × Months | Monthly Cost |  | Total
Project Manager | 1 × 6 months | 18000 |  | 108000
Site Engineer | 2 × 6 months | 11000 |  | 132000

## Cost & Budget
Al Fou'ah 3380 Students School — Cost & Budget
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Currency | AED
Client budget | 420000
Budget source | Client stated budget
Estimated cost | 367349
Sell price | 418777.86
Headroom against client budget | 1222.14
System | Budget | Estimated Cost | Variance | Variance % | Note
Access Control | 75000 | 79500 | -4500 | -6
CCTV | 120000 | 31840 | 88160 | 73.5 | Client allowance from concept stage
Containment | not set | 11620
Structured Cabling | not set | 4389
Total | 195000 | 127349 | 67651 |  | Excludes staff / preliminaries, which are not budgeted per system.

## Product Recommendations
Al Fou'ah 3380 Students School — Product Recommendations
Dubai, UAE · Bill of Quantities · Generated 8/17/2026, 5:38:25 PM
AI-generated estimate — provided "as is," for informational purposes only, without warranty of any kind. Not a substitute for review, verification, or certification by a licensed engineer. User assumes full responsibility for independently verifying all quantities, specifications, and costs before tendering, procurement, or construction. Quantora accepts no liability for its use.
Verify availability, local approval and current model status before specifying or ordering. A brand named in the specification takes precedence over any suggestion below it; a catalogue entry is a suggestion, not an approved submittal.
Source | System | Applies To | Manufacturer / Specified Brands | Model | Tier | Country / Origin | Specification | Notes | Certifications Required | Clause | Page | Datasheet
Named in the project specification | CCTV | Fixed Dome Camera — internal areas | Axis, Hanwha, Bosch |  |  | EU, USA, Japan or Korea | Internal dome cameras to classrooms, corridors and lobbies, recording to the central VMS. | An approved equal may be offered, subject to technical review. | SIRA approval, CE | 27 20 10.3 | 148
Named in the project specification | CCTV | Network Video Recorder / VMS Server | Milestone, Genetec |  |  |  | Central recording with 31 days retention at full frame rate. | This brand list is closed — no approved equal is permitted. | SIRA approval | 27 20 10.7 | 151
Named in the project specification | Access Control | Card Reader — classroom and office doors | HID, Suprema |  |  |  | Proximity reader at every controlled door, integrated with the central ACS. | An approved equal may be offered, subject to technical review. | SIRA approval | 28 13 00.4 | 163
Catalogue suggestion | Access Control | card reader | HID Global | Signo 20 | premium |  | MIFARE DESFire EV3, OSDP v2, PoE option | Named in the specification |  |  |  | https://www.hidglobal.com
Catalogue suggestion | CCTV | dome camera | Axis Communications | P3265-LV | premium |  | 2MP/4MP dome, Lightfinder 2.0, PoE, IK10 | Named in the specification and holds local approval | Widely SIRA approved in Dubai |  |  | https://www.axis.com
Catalogue suggestion | CCTV | dome camera | Hanwha Vision | XND-8081RV | mid |  | 5MP dome, motorised varifocal, IP67 IK10 | Meets the 4MP varifocal requirement at a lower rate |  |  |  | https://hanwhavision.com
Manufacturer directory | Access Control |  | Bosch Security Systems |  | Premium | Germany |  | Premium tier — commonly named in consultant specifications.
Manufacturer directory | Access Control |  | Dahua Technology |  | Mid | China |  | Mid tier — usually accepted as an approved equal on technical merit.
Manufacturer directory | CCTV |  | Bosch Security Systems |  | Premium | Germany |  | Premium tier — commonly named in consultant specifications.
Manufacturer directory | CCTV |  | Dahua Technology |  | Mid | China |  | Mid tier — usually accepted as an approved equal on technical merit.
Manufacturer directory | Containment |  | OBO Bettermann |  | Premium | Germany |  | Premium tier — commonly named in consultant specifications.
Manufacturer directory | Containment |  | Panduit |  | Premium | United States |  | Premium tier — commonly named in consultant specifications.
Manufacturer directory | Structured Cabling |  | Panduit |  | Premium | United States |  | Premium tier — commonly named in consultant specifications.